## Sheet1
No | Conduite Material | Recommended values for
|  | New Pipes (A) | Design
1 | Unlined metallic pipes
| Cast iron, Ductile iron | 130 | 100
| Mid steel | 140 | 100
2 | Centrifugally lined metallic pipes
Cast iron, Ductile iron, and Mid-steel pipes lined with cement mortar or epoxy
| Up to 1200 mm dia | 140 | 140
| Above 1200 mm dia | 145 | 145
3 | Projection method cement mortar lined metallic pipes
| Cast iron, Ductile iron, and Mid-steel pipes | 130(B) | 110©
4 | Non-metallic pipes
| RCC spun concrete up to 1200 mm diameter | 140 | 140
| RCC spun concrete Above 1200 mm diameter | 145 | 145
| Pre-stressed spun concrete up to 1200 mm diameter | 140 | 140
| Pre-stressed spun concrete Above 1200 mm diameter | 145 | 145
| Asbestos cement | 150 | 150
| HDPE, UPVC, grp, frp | 150 | 140